## Slide 1
Stability Modelling and Analysis of Converter Driven Power System
Bikash Pal
Professor, Imperial College London

## Slide 2: Overview
Stability in recent context
Modelling
Analysis
Insight
Recommendations

## Slide 3: Time Scales of Power System Dynamic Phenomena
electromagnetic phenomena
electromechanical phenomena
Time scales for various classes of dynamic phenomena in power systems
electromechanical transients enabled several simplifications in characterization and analysis of the related phenomena
  Phasors approach

## Slide 4: New classification diagram
Definition and Classification of power system stability
New (in)stability categories
motivated by the increasing use of converter-interfaced generators

## Slide 5: Time-scale representation aspects
Definition and Classification of power system stability
Electromagnetic transient modeling required
Phasor domain modeling is appropriate

## Slide 6: Recent incidence in UK Transmission
On 24/08/2021 severe voltage disturbances were observed on the SSEN-T and SPEN transmission systems.
Major disturbance lasted 20-25 seconds on two occasions, approx. 30 minutes apart
Investigation of available data suggests:
    The oscillations with the largest magnitude were in the north of Scotland
    The oscillations had a frequency of ≈8 Hz
Some Users tripped off during the disturbances

## Slide 7: Impedance scanning
Iinj, IBR(ω)=YIBR(ω)Vinj(ω)
Vinj(ω)=ZIBR(ω) Iinj, IBR(ω)
For strong grids, there is:
Zth(ω)<<1/YIBR(ω)
Zth(ω)YIBR(ω) <<1
Iinj, grid(ω) >>Iinj, IBR(ω)

## Slide 8: 39 Bus system in PSCAD
Dynamic response for fault on Bus 16 cleared after 180 [ms]
EMT simulation
RMS simulation
@Kundur’s book
~8 RPM
~20 deg

## Slide 9: Impedance approach to stability modelling: frequency-domain
Real transfer functions
Complex transfer functions

## Slide 10: Impedance approach
Real transfer functions
Complex transfer functions

## Slide 11: Objective
Measure
Use for stability
Limitation
Limited to only a single converter to infinite-bus scenario
System identification problem is “not trivial”
Real transfer functions
Complex transfer functions

## Slide 12: Impedance estimation
Real transfer functions
4 unknowns
2 equations
At least 2 measurements tests
Test 1
Test 2
G. Francis, R. Burgos, D. Boroyevich, F. Wang and K. Karimi, "An algorithm and implementation system for measuring impedance in the D-Q domain," 2011 IEEE Energy Conversion Congress and Exposition, Phoenix, AZ, 2011, pp. 3221-3228, doi: 10.1109/ECCE.2011.6064203.

## Slide 13: Impedance estimation: approximation
Real transfer functions
Vector fitting
4 unknowns
At least 2 measurements tests

## Slide 14: Impedance estimation: Vector fitting
Example: average model of VSC with PLL and current control
A. Rygg and M. Molinas, "Apparent Impedance Analysis: A Small-Signal Method for Stability Analysis of Power Electronic-Based Systems," in IEEE Journal of Emerging and Selected Topics in Power Electronics, vol. 5, no. 4, pp. 1474-1486, Dec. 2017

## Slide 15: Impedance estimation: Vector fitting
Example reproduced in PSCAD: average model of VSC with PLL and current control
measurements
fitting

## Slide 16: Impedance estimation: Vector fitting
Example reproduced in PSCAD: average model of VSC with PLL and current control including delay
measurements
fitting

## Slide 17: Impedance estimation: Vector fitting
Example: MMC STATCOM with detailed control structure
measurements
fitting

## Slide 18: Admittance estimation: Vector fitting
Example: MMC STATCOM with detailed control structure (SCR =10.0)
measurements
fitting

## Slide 19: Admittance estimation: Vector fitting
Example: MMC STATCOM with detailed control structure (SCR =1.0)
measurements
fitting

## Slide 20: Impact of Time step for frequency sweep on admittance
The MMC STATCOM model uses a carrier with a frequency of 360 [Hz], and each arm has 44 power modules, the effective update frequency is 15,840 [Hz]. In this case, the solution time-step should be at most 63 [μs].
Time step 10 [μs]
Time step 60 [μs]
Time step 100 [μs]

## Slide 21: Impact of frequency sweep time step on admittance
Example: MMC STATCOM with detailed control structure (SCR =1.0)
measurements
fitting

## Slide 22: Impact of Measurement delay on stability margin
Measurement delays reduce significantly the stability margin of the STATCOM module

## Slide 23: Stability analysis of power systems
Synchronous machines
STATCOM (MMC)
Wind Farm (VSC)
Networks
Loads

## Slide 24: 39 Bus system in PSCAD
39 Bus system in 345 [kV]
Analogue to the DigSILENT PowerFactory system
Synchronous machines with AVR, Governor and steam turbine dynamics
Lines modelled as π-circuits

## Slide 25: 39 Bus system in PSCAD
Dynamic response for fault on Bus 16 cleared after 180 [ms]
EMT simulation
RMS simulation

## Slide 26: 39 Bus system in PSCAD
STATCOM

## Slide 27: 39 Bus system in PSCAD : Test case for stability analsys

## Slide 28: 39 Bus system in PSCAD

## Slide 29: Stability analysis for varying grid strength (WF only)
Sensitivity over the grid strength at V1 by varying

## Slide 30: Stability analysis for varying grid strength (WF only)
Results in reduced system

## Slide 31: Impact of STATCOM AC voltage loop gain on stability
31

## Slide 32: STATCOM loop gain Kpv on relative contribution to stability

## Slide 33: Validation in full 39 bus PSCAD model
PSCAD results full 39 bus system, changes on proportional gain

## Slide 34: Insights
Impedance estimation-based stability assessment tool takes care of the detail dynamic model of MMC technology
The model is comprehensive in assessing the network stability impact of control delay, varying network strength and fault ride through (FRT) capability of these devices during network events

## Slide 35: Insights
The approach has demonstrated that real network operability margin is significantly lower in low short circuit cases when compared to the same obtained through time average simplified model of these devices.
This does not model control and converter limit and saturations.

## Slide 36: Recommendations
It is very much required to have detailed models of converter-based devices when performing grid connection studies in Electro-Magnetic Transient (EMT) time scale
Stability assessment studies need to be performed for varying grid strengths/short circuit level at the point of connection as well as transmission voltage levels.

## Slide 37: Recommendations
TNO should insist on various other parametric sensitivity studies regarding key control schemes, interface PLL technologies etc.
The grid connection study specification should be amended with these requirements so that any connection study adheres to these specifications.

## Slide 38: Researcher
Dr Nicolas Cifuentes
  MEng , Universidad de Chile
  PhD , Imperial College London
1. N. A. Cifuentes Otto, M. Sun, R. Gupta and B. C. Pal, "Black-Box Impedance-Based Stability Assessment of Dynamic Interactions Between Converters and Grid," in IEEE Transactions on Power Systems
2. N. Cifuentes and B. C. Pal, "A New Approach to the Fault Location Problem: Using the Fault’s Transient Intermediate Frequency Response," in IEEE Open Access Journal of Power and Energy, vol. 8, pp. 510-521, 2021,

## Slide 39
Estimation
Monitoring
Control
Modelling
Researchers
Yanshu
Adeyemi
Sai
Dr Guo
Mert
Dr Firdous
Jintao
Dr Wu
Sowmya
Malek
Dr Yang

## Slide 40
Estimation
Monitoring
Control
Modelling
Researchers
Onyema
Adeyemi
Diptargha
Dr Yang
Mert
Dr Guo
Kevin
Dr Firdous
Jintao
Dr Wu
Dr Kampitsis
Malek
Sai
Sowmya
Yanshu

## Slide 41
Estimation
Monitoring
Control
Modelling
Researchers
Onyema
Adeyemi
Diptargha
Ali
Mert
Dr Guo
Kevin
Dr Firdous
Magne
Jintao
Dr Wu
Dr Kampitsis
Malek
Sai
Andrea
Sowmya
Yanshu

## Slide 42: Our funding supports

## Slide 43: Comments or Questions